# GIF Series (Medium to High Volume FRP Fans)

SPECIFICATIONS

# General

- The fan is designed and constructed so that the gas stream only contacts solid FRP surfaces.

- All steel fasteners within the gas contact area will be stainless steel and encapsulated with a minimum of 0.1875" (3 mm) of FRP lay-up.

- All fan shafts will be fully protected from exposure to the gas stream with FRP shaft sleeves.

- The fan shall be constructed as per AMCA Standards 99.

- Manufacture of acceptance: Plasticair Inc.

# Air Performance

- The performance ratings are to be in accordance with AMCA standard 210.

- The fan must bear the AMCA Air & Sound Performance Seal.

- Alternate bidders must not exceed scheduled RPM, Sound levels or BHP.

# Impeller Construction

- The impeller is to be of a high efficiency backward inclined design.

- The material of construction is to be vinyl ester resin (premium quality Derakane 510) and reinforcing glass throughout.

- The method of construction is to be hand lay-up only.

- The entire surface of the impeller exposed to the gas stream will be complete with a resin rich corrosion barrier consisting of C-veil and a smooth finish.

- Impeller will be constructed of clear resin to detect imperfections.

- The shaft is to be attached to the back-plate of the impeller by way of a taper lock bushing and a one-piece sprocket hub. The entire shaft attachment assembly is to be completely covered with a minimum 0.25"(6 mm) of FRP lay-up.

- Radial blade fans are not permitted.

# Housing Construction

- The fan housing is solid FRP throughout. The outlet and inlet flanges are to be of heavy industrial quality. All flanges are to have factory flat finishes.

- The material of construction will be vinyl ester resin (premium quality Derakane 510) and reinforcing glass throughout.

- The method of construction will be hand lay-up only. The entire surface exposed to the gas stream will be complete with a resin-rich corrosion barrier consisting of C-veil and a smooth finish. The outer surface of the housing will be of a heavy UV stabilized gel coat.

- The housing shall include a machined Teflon shaft seal to limit gas leakage.

- A sound enclosure is not permitted.

# Steel Fan Base

- The fan base is to be of a heavy-duty industrial quality design to minimize vibration and to ensure long life. The bearing shaft pedestal is to be constructed of heavy gauge steel.

- The fabrication method is to be all welded.

- After welding is complete, prior to the fan assembly, the fan base is to be sandblasted white and cladded with FRP to a total of 3/16” thickness.

- The base is to be rust proof.  Painted bases are not acceptable.

# Bearings

- Bearings are to be solid pillow block, self-aligning type or split pillow block.

- The bearings are to be rated and designed for a minimum L-10 life of 200,000 hours.

- The bearings are to be located out of the air stream.

- The method of lubrication will be grease per the motor manufacturer’s recommendations.

# Shaft

- Fan shaft will be 1045 carbon steel complete with the correct keyways to accept V-belt drive selections.

- The diameter of the shaft shall be sized to ensure that the critical speed of the fan is at least 25% above the fan operating speed.

- The impeller side of the shaft shall be complete with an FRP shaft sleeve, which is bonded to the back-plate of the impeller and protrudes through the housing.

- The outside diameter of the sleeve is machined to provide a minimum clearance gap with the Teflon shaft seal.

# Motor

- Motor will be a foot mounted totally enclosed fan cooled motor with a 1.15 service factor.

# Belt Drive

- V-belt drive shall be sized with a safety factor of 1.5 times the motor horsepower.

- An adjustable base will be provided under the motor to permit setting the belt tension.

# Guards

- Weatherproof FRP guards complying with the OSHA standard will protect the shaft and v-belt drive.

- Guards will be vented for proper motor ventilation.

# Balancing and Testing

- Balancing of the impeller shall be achieved only with the use of the identical material used to fabricate the impeller. Balancing shall be in accordance with ASTM D-4167.

- The fan shall be test run at operating speed and not shipped until vibration readings are within acceptable limits.

- Records shall be maintained and a written copy shall be available upon request.

# Flame spread rating

- If indicated on the fan scheduled 0-25 flame spread is required; fan housing and impeller will be constructed of Derakane 510-C throughout and will meet ASTM-E84 class 1 (0-25 flame spread).

# Warranty

- The supplier shall warrant that all fan components shall be free from defects in materials and workmanship for a period of 15 months from date shipped or 12 months from equipment startup, whichever occurs first.