# 900-T Series (Tube Axial FRP Fans)

SPECIFICATIONS

# General

- The fan is designed and constructed so that the gas stream only contacts solid FRP surfaces.

- All steel fasteners within the gas contact area will be stainless steel and encapsulated with a minimum of 0.1875" (3 mm) of FRP lay-up.

- All fan shafts will be fully protected from exposure to the gas stream with FRP shaft sleeves.

- The fan shall be constructed as per AMCA Standards 99.

- Fans shall be tested to ANSI/AMCA 210 and AMCA 300.

- All Electrical components will be CSA/UL compliant and meet NEMA standards

Manufacture of Acceptance:     Plasticair Fan Company | Division of Plasticair Inc.

# Air Performance

- The performance ratings of equal or alternate bidders shall not exceed any of the following: scheduled performance characteristics by more than 5%; revolutions per-minute, horse power, or sound levels.

- Supplied fans must be able to achieve 10% variation in static pressure without a motor change.

- Fan must bear the AMCA Air and Sound Seal.

# Propeller Construction

- The 6 bladed propeller is to be a full width, full twist design.

- The material of construction is to be vinyl ester resin (premium quality Derakane 510) and reinforcing glass throughout.

- The method of construction is to be hand lay-up only.

- The entire surface of the propeller exposed to the gas stream will be complete with a resin rich corrosion barrier consisting of C-veil and a smooth finish.

- Propeller will be constructed of clear resin to detect imperfections.

- The shaft is to be attached to the back-plate of the propeller by way of a taper lock bushing and a one-piece sprocket hub.

- The entire shaft attachment assembly is to be completely covered with a minimum 0.25"(6 mm) of FRP lay-up.

# Housing Construction

- The fan housing shall be tubular flow through design.

- The method of construction is to be hand lay-up only.

- The entire surface of housing exposed to the gas stream will be complete with a resin rich corrosion barrier consisting of C-veil and a smooth finish minimum 90 mils thickness.

- All flanges are to have factory flat finishes.

- The outer surface of the housing will be of a heavy UV stabilized gel coat and grey in color.

- Fan housing shall be structurally designed to handle specified static pressure and reduce vibrations.

# Bearings

- The type and mountings of Bearings shall be designed for a minimum of L10 – 115,000 hours.

- Bearings shall be ball or spherical roller type.

- Mountings shall be solid pillow block or split pillow block.

- The successful bidder shall supply with the submittal package, the bearing calculation.

# Shaft

- Shaft material shall be 316 stainless steel, complete with correct keyways to accept V-belt drive selections.

- The diameter of the shaft shall be sized to ensure that the critical speed of the fan is at least 25% above the fan operating speed.

- The impeller side of the shaft shall be complete with an FRP shaft sleeve, which is bonded to the back-plate of the impeller and protrudes through the housing.

- The outside diameter of the sleeve is machined to provide a minimum clearance gap with the Teflon shaft seal.

- OPTIONAL Mechanical Shaft Seal. The impeller shaft shall be supplied with a minimum 0.1875” thick shaft sleeve fully covering the shaft throughout the seal. The Shaft seal shall be constructed of FRP, packed with Teflon, spring loaded and lithium grease filled

# Motor

- Motor will be a foot mounted totally enclosed fan cooled motor with a 1.15 service factor.

# Belt Drive

- V-belt drive shall be sized with a safety factor of 1.5 times the motor horsepower.

- An adjustable base will be provided under the motor to permit setting the belt tension.

# Guards

- Weatherproof FRP guards complying with the OSHA standard will protect the shaft and v-belt drive.

- Guards will be vented for proper motor ventilation.

# Balancing and Testing

- Balancing of the impeller shall be achieved only with the use of the identical material used to fabricate the impeller. Balancing shall be in accordance with ASTM D-4167 and meet the standard of G2.5.

- The fan shall be test run at operating speed and not shipped until vibration readings are within acceptable limits

# Option for Spark Resistant Construction

- Fan shall be constructed incorporating an electrically conductive layer of graphite within the gas contact corrosion barrier.

- Wheel and housing will be pigmented black.

- Grounding lugs and wire are to be used to provide a common grounding point for static electricity to safely purge.

# Flame spread rating

- FRP shall be 0-25 flame spread rated.

- Fan housing and impeller will be constructed of Derakane 510-C throughout and will meet ASTM-E84 class 1.

# Warranty

a) The supplier shall warrant that all fan components shall be free from defects in materials and    workmanship for a period of 15 months from date shipped or 12 months from equipment startup, whichever occurs first.