# DMF (INLINE MIXED FLOW FRP FAN)

SPECIFICATIONS

# General

- Fans and stacks shall be designed and constructed so that the gas stream only contacts solid FRP surfaces.

- Steel fasteners within the gas contact area will be stainless steel and encapsulated with a minimum of 0.1875" (3 mm) of FRP lay-up.

- Motor shafts will be fully protected from exposure to the gas stream by FRP shaft sleeves.

- The fan shall be constructed per AMCA Standards 99.

- The fan arrangement will be based on AMCA 99 and will be Direct Drive AMCA arrangement #4.

Acceptable Manufacturers:     Plasticair Inc.

# Air Performance

- The performance ratings are to be in accordance with AMCA FEG for Air and Sound. No other performance standard or test will be accepted.

- Fan manufactures catalog will be published and accessible from the AMCA web site certified ratings program.

- Sound levels, horse power levels and tip speed are not to exceed what is on the schedule.

# Housing Construction

- The multi bifurcated inline fan housing is to be solid FRP throughout.

- Housing is designed so that the motor is not exposed to the exhaust air.

- The outlet and inlet flanges are to be of heavy industrial quality.

- All flanges are to have factory flat finishes.

- The materials of construction will be vinyl ester resin (premium quality premium quality 0-25 flame spread) and reinforcing glass throughout.

- The entire surface exposed to the gas stream will be complete with a resin-rich corrosion barrier consisting of C-veil and a smooth finish.

- The outer surface of the housing will be of a heavy UV stabilized gel coat.

- The housing shall include a machined Teflon shaft seal to limit gas leakage.

# Impeller

- The impeller is to be of a high efficiency mixed flow design.

- The materials of construction will be vinyl ester resin and reinforcing glass throughout.

- The method of construction is to be hand lay-up only.

- Flame spread rating as per ASTM E84 is to be Class 1 (0-25).

- The entire surface of the impeller exposed to the gas stream will be complete with a resin-rich corrosion barrier consisting of C-veil and a smooth finish.

- The motor shaft is to be attached to the impeller by way of a taper lock bushing and a one piece cast sprocket hub.

- The entire shaft attachment assembly is to be completely covered with a minimum 0.25"(6 mm) of FRP lay-up.

- The attachment will be air tight and fully protected from the airstream.

# Bearings

- Motor bearings are to be minimum L-10 life of 110,000 hours.

# Motor

- Premium Efficiency Motor will be a foot mounted totally enclosed fan cooled motor with a 1.15 service factor.

- Motor will be VFD ready.

- Belt drive units are not acceptable.

# Balancing and Testing

- All fans shall be completely assembled and test run as a unit at the specified operating speed prior to shipment.

- Balancing of the impeller shall be achieved only with the use of the identical material used to fabricate the impeller.

- Balancing shall be in accordance with ASTM D-4167.

- The fan shall be test run at operating speed and not shipped until vibration readings are within acceptable limits. Acceptable limits are as per G2.5.

- Records shall be maintained and a written copy shall be available upon request.

# Warranty

- The supplier shall warrant that all system components shall be free from defects in materials and workmanship for a period of 15 months from date shipped or 12 months from equipment start up, whichever occurs first.